## Info
This file contains the raw and analysed data on service lives. It is part of the Data in Brief paper entitled:
Dataset of service life data of 100 building elements and technical systems including their descriptive statistics and fitting to lognormal distribution model
Authors: Kyriaki Goulouti1, Didier Favre1 , Morgane Giorgi1, Pierryves Padey1, Alina Galimshina2, Guillaume Habert2, Sébastien Lasvaux1
Affiliations
1 Solar Energy and Building Physics Laboratory, Institute of Thermal Engineering, University of Applied Sciences of Western Switzerland (HES-SO), Avenue de Sports 20, 1401, Yverdon-les-Bains, Switzerland
2 Chair of Sustainable Construction, Institute of Construction and Infrastructure Management, Swiss Federal Institute of Technology (ETH Zurich), Stefano Franscini Platz 5, 8093, Zurich, Switzerland
Corresponding author(s)
sebastien.lasvaux@hes-so.ch, +41 24 557 61 87

## Data
Code | Level 1 | Level 2 | Level 3 | Level 4 | Number of data | Min | Decile 1 | Quartile 1 | Median=Quartile 2 | Quartile 3 | Decile 9 | Max | meanlog | sdlog | p-value
C | Structural work |  |  |  | 71 | 20 | 35 | 50 | 75 | 93.1562 | 120 | 135.5417 | 4.2036 | 0.43366 | 0.35609
C 1 |  | Slab, foundations |  |  | 40 | 23 | 29.9375 | 47.5 | 77.5 | 100 | 111 | 150 | 4.1658 | 0.50891 | 0.31187
C 2 |  | Load-bearing wall |  |  | 54 | 30.2917 | 47.1667 | 55.4167 | 80 | 100 | 100 | 145.6667 | 4.3045 | 0.35238 | 0.22891
C 2.1a |  |  | Load-bearing wall (underground) |  | 36 | 30.3333 | 50 | 57.5 | 77.5 | 100 | 100 | 150 | 4.2898 | 0.35831 | 0.42286
C 2.1b |  |  | Load – bearing wall (above ground) |  | 49 | 30.25 | 44.95 | 60 | 76.8 | 100 | 100 | 150 | 4.289 | 0.35803 | 0.29516
C 2.2 |  |  | Internal load-bearing wall |  | 33 | 45.6667 | 52 | 60 | 92.0833 | 100 | 110.8 | 137.9167 | 4.4232 | 0.29985 | 0.14523
C 3 |  | Columns |  |  | 21 | 20 | 50 | 65 | 93.75 | 100 | 120 | 129 | 4.3503 | 0.45555 | 0.201
C 4 |  | Load – bearing structure of slabs and roofs |  |  | 50 | 20 | 34.625 | 50 | 74.4792 | 89.8438 | 101.3333 | 120 | 4.1679 | 0.45827 | 0.22926
C 4.1 |  |  | Load – bearing structure of slabs |  | 34 | 28 | 60 | 75 | 90 | 100 | 114 | 127.5 | 4.4073 | 0.30842 | 0.29504
C 4.2 |  |  | Stairs, ramps |  | 29 | 15 | 30.1 | 50 | 73.5417 | 100 | 100 | 100 | 4.1102 | 0.50684 | 0.2803
C 4.3 |  |  | Balconies |  | 30 | 21 | 28.6 | 35 | 63.3333 | 85 | 100 | 120 | 4.0246 | 0.51838 | 0.29194
C 4.4 |  |  | Load – bearing structure of roofs |  | 38 | 30 | 50 | 60 | 75 | 89.375 | 106 | 125 | 4.3133 | 0.30385 | 0.85626
D | Technical systems |  |  |  | 73 | 13.25 | 17.1 | 20 | 25.625 | 30.9167 | 41.3333 | 50 | 3.2517 | 0.33397 | 0.85218
D 1 |  | Electrical installations |  |  | 64 | 8.1044 | 15 | 20 | 30 | 38.5 | 50 | 80 | 3.3242 | 0.46328 | 0.683
D 1.3 |  |  | Lighting |  | 25 | 2 | 8.4 | 11.2417 | 20 | 25 | 25 | 40 | 2.7605 | 0.65379 | 0.27995
D 1.2a |  |  | Photovoltaics |  | 10 | 11.5 | 16.9 | 19.0625 | 21.75 | 25 | 30 | 30 | 3.063 | 0.26975 | 0.92723
D 2 |  | Building automation |  |  | 29 | 5 | 10 | 15 | 20 | 25 | 50 | 100 | 3.0021 | 0.66992 | 0.31054
D 3 |  | Security installation |  |  | 16 | 5 | 7.5 | 10.45 | 15 | 20 | 20 | 40 | 2.6432 | 0.51927 | 0.57571
D 4 |  | Fire protection installation |  |  | 21 | 10 | 10 | 15 | 20 | 30 | 37.5 | 50 | 2.9846 | 0.45594 | 0.76198
D 5 |  | Heating system |  |  | 66 | 13 | 15 | 18.6159 | 24.4023 | 30 | 34.489 | 80 | 3.1754 | 0.35053 | 0.59249
D 5.1 |  |  | Fuel storage |  | 23 | 10 | 16.7667 | 22.75 | 30 | 35 | 45 | 70 | 3.318 | 0.45853 | 0.69624
D 5.2 |  |  | Heat production |  | 61 | 5 | 13.2889 | 15 | 18.75 | 21.72 | 25 | 30 | 2.9055 | 0.2949 | 0.544
D 5.2a |  |  |  | Boiler | 34 | 13.4 | 15 | 18.625 | 20 | 24.5 | 25 | 40 | 3.0231 | 0.22465 | 0.54534
D 5.2c |  |  |  | Heat pump | 27 | 10 | 11.2667 | 14 | 15 | 20 | 21.7 | 25 | 2.7639 | 0.25369 | 0.90789
D 5.2f |  |  |  | Geothermal probes | 4 | 23 | 25.1 | 28.25 | 32.5 | 36.25 | 38.5 | 40 | Fitting impossible due to the limited number of available data
D 5.2d |  |  |  | Solar collector system | 19 | 10 | 19 | 20 | 20 | 20.5 | 26 | 30 | 3.0128 | 0.22808 | 0.068848
D 5.2e |  |  |  | Water – heater | 39 | 2.5 | 10.92 | 15 | 18.3333 | 20 | 25 | 40 | 2.8141 | 0.41886 | 0.092384
D 5.3 |  |  | Heat distribution |  | 34 | 13.8333 | 16.25 | 18.3438 | 27.0417 | 35 | 60 | 80 | 3.3454 | 0.4833 | 0.66644
D 5.4 |  |  | Heat emission |  | 32 | 15 | 19.454 | 20.8438 | 28.75 | 35 | 48.125 | 80 | 3.3634 | 0.37719 | 0.81736
D 6 |  | Refrigeration system |  |  | 30 | 5 | 10.9 | 14.625 | 19.0806 | 20 | 25.5 | 45 | 2.8446 | 0.42021 | 0.59332
D 7 |  | Ventilation and air conditioning systems |  |  | 51 | 12 | 17.4444 | 20 | 22.2222 | 26.1111 | 32.5 | 50 | 3.1497 | 0.29883 | 0.13616
D 7.1 |  |  | Air supply, air extraction |  | 21 | 5 | 10 | 17.5 | 20 | 30 | 30 | 60 | 3.008 | 0.51946 | 0.64938
D 7.2 |  |  | Air conditioning |  | 22 | 8 | 10.35 | 15 | 17.9167 | 24.1667 | 30 | 40 | 2.883 | 0.42307 | 0.93324
D 7.3 |  |  | Air central distribution |  | 27 | 20 | 24 | 26.25 | 30 | 36.6667 | 47 | 60 | 3.4642 | 0.26652 | 0.88701
D 7.4 |  |  | Air supply |  | 14 | 15 | 20 | 20 | 20 | 25 | 28.5 | 40 | 3.1125 | 0.22519 | 0.37346
D 7.5 |  |  | Small ventilation systems |  | 9 | 15 | 19 | 20 | 30 | 30 | 32 | 40 | Fitting impossible due to the limited number of available data
D 8 |  | Water, gaz and compressed air distribution system |  |  | 54 | 10 | 20 | 25.0116 | 30 | 44.5833 | 50 | 60.8571 | 3.4557 | 0.37309 | 0.61464
D 8.0 |  |  | Sanitary installations |  | 27 | 20 | 20 | 22.5 | 30 | 38 | 50 | 60 | 3.4177 | 0.33092 | 0.34746
D 9 |  | Transportation system |  |  | 25 | 8 | 15 | 20 | 25.5 | 35 | 40 | 50 | 3.2138 | 0.44232 | 0.71086
D 9.1 |  |  | Elevators |  | 25 | 8 | 15.35 | 20 | 29 | 35 | 40 | 50 | 3.2333 | 0.43443 | 0.60422
E | Façade elements and coatings |  |  |  | 91 | 10 | 17.5 | 22.125 | 31.3022 | 42.2361 | 53.3187 | 100 | 3.4377 | 0.47639 | 0.88353
E 1 |  | Wall coatings against ground |  |  | 31 | 17 | 24 | 30 | 41 | 60 | 80 | 100 | 3.7382 | 0.47184 | 0.97702
E 1.1 |  |  | Impermeability against ground |  | 19 | 17 | 24.8 | 35 | 50 | 60 | 82 | 100 | 3.836 | 0.46929 | 0.95159
E 1.2 |  |  | Thermal insulation against ground |  | 16 | 20 | 25 | 30 | 40 | 65 | 85 | 100 | 3.7682 | 0.48871 | 0.80546
E 2 |  | External wall coatings |  |  | 78 | 5 | 10 | 20 | 35 | 47.6667 | 68.425 | 100 | 3.3844 | 0.67546 | 0.19221
E 2.0 |  |  | Internally insulated façade |  | 35 | 17 | 27.5 | 39.1667 | 50 | 78.3333 | 100 | 100 | 3.929 | 0.4866 | 0.5608
E 2.1 |  |  | Wall coatings of non-insulated façade |  | 64 | 5 | 10 | 11.5 | 25.7917 | 40 | 54.2562 | 120 | 3.1469 | 0.7173 | 0.43395
E 2.2 |  |  | Compact façade |  | 41 | 21.6667 | 25 | 30 | 37.6667 | 45.1667 | 56 | 80 | 3.6305 | 0.32256 | 0.72274
E 2.2a |  |  |  | Insulation | 31 | 25 | 30 | 30 | 37.5 | 55 | 100 | 100 | 3.8077 | 0.45828 | 0.12508
E 2.2b |  |  |  | Rendering | 34 | 5 | 17.9 | 25 | 33.3333 | 48.125 | 52.1 | 65 | 3.4294 | 0.516 | 0.38915
E 2.3 |  |  | Ventilated façade |  | 40 | 20 | 27.2917 | 37.625 | 43.1369 | 54.6875 | 62.3 | 90 | 3.7759 | 0.34391 | 0.83343
E 2.3a |  |  |  | Insulation with fixings | 30 | 25 | 30 | 35 | 40 | 71.25 | 100 | 100 | 3.8756 | 0.45695 | 0.18761
E 2.3b |  |  |  | Cladding | 33 | 30 | 30 | 40 | 50 | 60 | 70.2714 | 100 | 3.8806 | 0.32576 | 0.68211
E 2.4 |  |  | Lightweight façade |  | 25 | 24.2857 | 25.4 | 35 | 41.9048 | 60 | 100 | 120 | 3.8222 | 0.46638 | 0.45647
E 2.5 |  |  | External ceiling cladding |  | 55 | 5 | 7.4 | 10 | 14 | 28.45 | 49.4 | 80 | 2.7853 | 0.73935 | 0.22446
E 2.6 |  |  | Safety barriers |  | 13 | 25 | 32 | 45 | 52.5 | 76.6667 | 82.6667 | 100 | 3.9937 | 0.38878 | 0.98713
E 3 |  | Windows, doors |  |  | 77 | 5 | 18.8074 | 25 | 30 | 38.3333 | 50 | 60 | 3.3736 | 0.43132 | 0.23166
E 3.1 |  |  | Windows |  | 68 | 5 | 17.0867 | 23.25 | 30 | 40 | 50 | 60 | 3.37 | 0.45607 | 0.49336
E 3.1a |  |  |  | Wood frame windows | 11 | 20 | 25 | 30 | 40 | 50 | 50 | 60 | 3.6164 | 0.32203 | 0.93873
E 3.1b |  |  |  | Metal frame windows | 11 | 18.3333 | 23 | 28.5 | 40 | 50 | 60 | 60 | 3.6046 | 0.38127 | 0.89582
E 3.1c |  |  |  | Wood-metal frame windows | 5 | 25 | 31 | 40 | 40 | 50 | 56 | 60 | Fitting impossible due to the limited number of available data
E 3.1d |  |  |  | Synthetic frame windows | 11 | 16 | 21 | 25 | 30 | 45 | 50 | 50 | 3.4701 | 0.36742 | 0.85769
E 3.2 |  |  | External doors |  | 52 | 5 | 15.8583 | 23.9479 | 30 | 43.3611 | 50 | 60 | 3.4017 | 0.49604 | 0.50595
E 3.3 |  |  | Sun protection |  | 36 | 5 | 10 | 17.7083 | 25 | 31.0417 | 45 | 60 | 3.1446 | 0.55439 | 0.56533
F | Roof elements |  |  |  | 91 | 15 | 22.5 | 30 | 35 | 40 | 50 | 100 | 3.5319 | 0.35337 | 0.32571
F 1 |  | Covering |  |  | 83 | 15 | 20.175 | 29.375 | 35 | 40 | 53.5417 | 100 | 3.5205 | 0.37293 | 0.43744
F 1.1 |  |  | Underground impermeability |  | 9 | 20 | 28 | 30 | 40 | 60 | 64 | 80 | Fitting impossible due to the limited number of available data
F 1.2 |  |  | Flat roof |  | 62 | 15 | 20 | 25.2743 | 30 | 39.707 | 50 | 100 | 3.4569 | 0.39554 | 0.25652
F 1.3 |  |  | Sloping roof |  | 58 | 15 | 25 | 35.9375 | 40 | 50 | 75 | 100 | 3.7223 | 0.40565 | 0.46367
F 1.4 |  |  | Lightning protection |  | 10 | 20 | 24.5 | 30 | 40 | 50 | 50 | 50 | 3.6043 | 0.31536 | 0.61139
F 2 |  | Integrated elements in roofs |  |  | 58 | 15 | 21.2688 | 25.5417 | 30 | 40.0625 | 50 | 100 | 3.497 | 0.37584 | 0.56056
F 2.1 |  |  | Integrated elements in flat roofs |  | 50 | 15 | 20 | 25 | 30 | 37.8767 | 45.5 | 60 | 3.4033 | 0.31154 | 0.84546
F 2.1a |  |  |  | Wood frame window | 17 | 25 | 30 | 30 | 30 | 30 | 37 | 50 | 3.4512 | 0.14644 | 0.035608
F 2.1b |  |  |  | Metal frame window | 20 | 15 | 18 | 22.25 | 30 | 32.5 | 50 | 60 | 3.3686 | 0.37697 | 0.60361
F 2.1c |  |  |  | Synthetic frame window | 14 | 14 | 20 | 20.5 | 30 | 37.5 | 40 | 50 | 3.3326 | 0.34257 | 0.66752
F 2.2 |  |  | Integrated elements in sloping roofs |  | 30 | 15 | 21.6875 | 26.2812 | 33 | 46.6667 | 54.475 | 70 | 3.5364 | 0.37762 | 0.9305
F 2.2a |  |  |  | Wood frame fixed window | 11 | 30 | 30 | 30 | 30 | 32.5 | 40 | 50 | 3.4878 | 0.16095 | 0.081965
F 2.2b |  |  |  | Metal frame fixed window | 12 | 15 | 19.1 | 23 | 30 | 41.25 | 49.5 | 60 | 3.4182 | 0.39968 | 0.99912
F 2.2c |  |  |  | Wood frame casement window | 11 | 20 | 30 | 30 | 30 | 32.5 | 40 | 50 | 3.4509 | 0.21419 | 0.27112
F 2.2d |  |  |  | Sliding metal frame window | 14 | 15 | 18.6 | 24 | 30 | 37.5 | 48.5 | 60 | 3.3952 | 0.37565 | 0.8975
F 2.2e |  |  |  | Metal frame casement window | 15 | 18 | 23.2 | 28 | 30 | 35 | 48 | 60 | 3.4512 | 0.30131 | 0.50329
G | Interior layout |  |  |  | 86 | 5 | 16.4306 | 20.3854 | 33.1389 | 42.659 | 54.8806 | 100 | 3.4398 | 0.51839 | 0.76506
G 1 |  | Partition wall, doors |  |  | 62 | 15 | 21.0667 | 30 | 40 | 50 | 65.875 | 96.5278 | 3.635 | 0.43461 | 0.95437
G 1.1 |  |  | Fixed partitions, non-load-bearing internal walls |  | 46 | 5 | 25 | 30 | 50 | 75 | 100 | 127.5 | 3.8371 | 0.63432 | 0.52213
G 1.2 |  |  | Portable partitions |  | 15 | 20 | 25.5 | 30 | 35 | 50 | 60 | 80 | 3.6398 | 0.36977 | 0.9343
G 1.3 |  |  | Internal windows |  | 20 | 5 | 15 | 25 | 33.75 | 60 | 75.5 | 100 | 3.507 | 0.73611 | 0.84698
G 1.4 |  |  | Internal doors |  | 55 | 5 | 16.55 | 25 | 30 | 49.4444 | 60 | 80 | 3.4825 | 0.53949 | 0.50973
G 2 |  | Flooring |  |  | 69 | 5 | 15.8 | 23.4 | 35 | 40.1354 | 51.7583 | 120 | 3.4025 | 0.55172 | 0.61337
G 2.1 |  |  | Support for flooring |  | 26 | 25 | 30 | 40 | 50 | 67.5 | 80 | 100 | 3.9261 | 0.36584 | 0.88368
G 2.2 |  |  | Finished flooring |  | 57 | 5 | 12 | 18 | 25 | 40 | 50.0741 | 120 | 3.2227 | 0.61388 | 0.86751
G 3 |  | Wall and column coverings |  |  | 67 | 4 | 11.5 | 21.125 | 30 | 43.5714 | 58.9333 | 100 | 3.3888 | 0.63356 | 0.32059
G 3.1 |  |  | Supports for wall covering |  | 19 | 10 | 19 | 30 | 40 | 55 | 84 | 120 | 3.6406 | 0.60455 | 0.95055
G 3.2 |  |  | Finished wall covering |  | 52 | 4 | 10 | 19.5792 | 30 | 43.8571 | 58.2 | 100 | 3.2843 | 0.71406 | 0.43822
G 4 |  | Ceiling covering |  |  | 60 | 10 | 15.45 | 20 | 36.5 | 50 | 60 | 100 | 3.463 | 0.55588 | 0.52202
G 4.2 |  |  | Finished ceiling coverings |  | 56 | 5 | 15.25 | 20 | 36.5 | 50 | 60 | 100 | 3.4447 | 0.60505 | 0.53132
G 5 |  |  |  |  | 50 | 5 | 16.675 | 20.1157 | 24.8611 | 36.4048 | 50 | 91.6667 | 3.2755 | 0.50236 | 0.55621
Note on A1: Author: code based on the adapted SN 506511 classification of building elements with additional levels of details for the DUREE database (from level 4)
Façade elements and coatings
F
G
C
E
D
Structural work
Technical installations
Roof elements
Internal layout
D5.2
D5.3
G.2
G.4
E2.2-E2.3-E2.4
E3.1
F1.3
G.3
E2.5
F1.2
D5.4
D.7
D1.2a
D5.2d
D.1
D5.2f
C
C4.3
D.8
E2.1
F2
G.1